**Description:**

Type: BROEN BALLOMAX

Art. No.: 63.602

Pressure: DN 015 to DN 050 = PN 40

DN 065 to DN 200 = PN 25

Dimension: DN 015 to DN 200

**Configuration:**

Fully welded branching valve with full bore and weld/weld connection. Especially designed for use in central heating, heating, cooling and industrial plants. Branching valve with plug for welding before insulation, ball with slot for direction indication. The valves are approved according to the directive for pressurized equipment PED 2014/68/EU, Module H. and manufactured according to ISO9001:2008 and ISO14001.

**Technical data:**

Connection: Weld/Weld

Temperature: Continuously 140 °C

Media: Treated water to avoid corrosion/lime formation

House: Steel P235GH (St. 37)

O-rings: EPDM and VITON

Ball: Stainless Steel AISI 304L

Seat packing: Reinforced PTFE 20%C

Operation: Unbraco key and/or wrench key

Surface: Environmentally corrosion resistant paint

**Labeling:**

Maker, Dimension, Pressure step, Temperature range, Production month and year.

CE marked